## New Tech Properties
Exchange rate (South African Reserve Bank, January 2024) | 18.35
| Fossil | [7 empty] | Large-Scale Nuclear (EPRI) |  |  |  |  | Small Modular Nuclear (EPRI) |  |  |  | Offshore wind |  |  | Solar thermal, parabolic trough | [5 empty] | Solar thermal, molten salt tower |  |  |  | Solar PV + Storage |  |  | Battery |  | Pumped Hydro
[15 empty] | NuScale | X-energy |  |  |  |  | Solar PT, 0hr | Solar PT, 3hr | Solar PT, 6hr | Solar PT, 9hr | Solar PT, 12hr |  | Solar MST, 3hr | Solar MST, 6hr | Solar MST, 9hr | Solar MST, 12hr
Technology | PC - 90% CO2 Wet cooling | Coal to Gas Dry cooling | 9F.05 Dry cooling | 9HA.02 Dry cooling | 2x1 9F.05 Dry cooling | 2x1 9HA.02 Dry cooling | 9 MW ICE Dry cooling | 18 MW ICE Dry cooling | Technology | 1x1600 MW, AREVA | 2x1600 MW, AREVA | 1x1117 MW, AP1000 | 2x1117 MW, AP1000 | Technology | 12x73 MW, SMR Dry cooling | Coal to SMR, 6x80 MW Dry cooling | Technology | OSW, fixed | OSW, floating | Technology | 0 h Storage | 3 h Storage | 6 h Storage | 9 h Storage | 12 h Storage | Technology | 3 h Storage | 6 h Storage | 9 h Storage | 12 h Storage | Technology | Solar + Storage | Technology | Li-ion | Technology | PHS
Rated capacity, MW net | 591 | 569 | 297.4 | 539.5 | 924.6 | 1591 | 9.5 | 16.2 | Rated capacity, MW net | 1600 | 3200 | 1117 | 2234 | Rated capacity, MW net | 876 | 480 | Rated capacity, MW | 800 | 800 | Rated capacity, MW net | 125 | 125 | 125 | 125 | 125 | Rated capacity, MW net | 125 | 125 | 125 | 125 | Solar PV, MWac | 250 | System size, MW | 100 | System size, MW | 1000
Plant cost estimates (2023) | [8 empty] | Plant cost estimates (2023) |  |  |  |  | Plant cost estimates (2023) | 73 |  | Plant cost estimates (2023) |  |  | Plant cost estimates (2023) | [5 empty] | Plant cost estimates (2023) |  |  |  |  | Solar PV, MWdc | 325 | Storage capacity, h | 4 | Storage capacity, h | 10
Total overnight cost, ZAR/kW | 149567.18 | 1113.845 | 12980.79 | 11158.635 | 18652.775 | 14336.855 | 61195.415 | 50168.9 | Total overnight cost, ZAR/kW | 176884.825 | 174680.99 | 169027.355 | 167263.92 | Total overnight cost, ZAR/kW | 153378.475 | 174583.735 | Total overnight cost, ZAR/kW | 72427.2894 | 107274.2205 | Total overnight cost, ZAR/kW | 83198.0087 | 110127.236 | 134718.3223 | 163898.1446 | 195044.5682 | Total overnight cost, ZAR/kW | 106474.7959 | 127822.9096 | 143208.6958 | 158985.1336 | Storage Capacity, MW | 100 | Energy storage, MWh | 400 | Energy storage, MWh | 10000
Lead times and project schedule (months) | 48 | 24 | 36 | 36 | 48 | 48 | 12 | 12 | Lead times and project schedule (months) | 72 | 84 | 72 | 96 | Lead times and project schedule (months) | 48 | 42 | Lead times and project schedule (months) | 36 | 36 | Lead times and project schedule, months | 48 | 48 | 48 | 48 | 48 | Lead times and project schedule, months | 48 | 48 | 48 | 48 | Energy storage, MWh | 400 | Plant cost estimates (January 2021) | 0 | Plant cost estimates (January 2021) | 0
Expense schedule, % of TPC per year | 10%, 25%, 45%, 20% | 95%, 5% | 16%, 46%, 39% | 16%, 46%, 39% | 4%, 17%, 51%, 29% | 4%, 17%, 51%, 29% | 100% | 100% | Expense schedule, % of TPC per year | 15%, 15%, 25%, 25%, 10%, 10% | 10%, 10%, 25%, 25%, 10%, 10%, 10% | 15%, 15%, 25%, 25%, 10%, 10% | 10%, 10%, 25%, 25%, 10%, 10%, 10% | Expense schedule, % of TPC per year | 15%, 35%, 35%, 15% | 15%, 35%, 35%, 15% | Expense schedule, % of TPC per year | 5%, 45%, 50% | 5%, 45%, 50% | Expense schedule, % of TPC per year | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | Expense schedule, % of TPC per year | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | 10%, 25%, 45%, 20% | Plant cost estimates (Jan 2023) |  | Total overnight cost, ZAR/kW | 25910.2 | Total overnight cost, ZAR/kW | 40010.34
Fuel cost estimates | [8 empty] | Fuel cost estimates | 0 | 0 | 0 | 0 | Fuel cost estimates | 0 |  | O&M cost estimates |  |  | O&M cost estimates | [5 empty] | O&M cost estimates |  |  |  |  | Total overnight cost, ZAR/kW | 25271.62 | Lead times and project schedule, months | 12 | Lead times and project schedule, months | 96
First year, ZAR/GJ | 41.7419 | 260.8866 | 260.8866 | 260.8866 | 260.8866 | 260.8866 | 260.8866 | 260.8866 | First year, ZAR/GJ | 15.3459 | 15.3459 | 15.3459 | 15.3459 | First year, ZAR/GJ | 15.3459 | 48.4896 | Fixed O&M, ZAR/kW/year | 2275.6811 | 1596.0886 | Fixed O&M, ZAR/kW/year | 1480.0441 | 1520.5933 | 1561.1424 | 1601.6916 | 1662.5153 | Fixed O&M, ZAR/kW/year | 1227.9247 | 1281.3127 | 1316.9047 | 1352.4968 | Lead times and project schedule, months | 12 | Expense schedule, % of TPC per year | 100 | Expense schedule, % of TPC per year | 12%,12%,12%,12%,12%,12%,12%,16%
Expected escalation (beyond inflation) | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Expected escalation (beyond inflation) | 0% | 0% | 0% | 0% | Expected escalation (beyond inflation) | 0% | 0% | Availability estimates | 93% | 93% | Variable O&M, ZAR/MWh | 0.7312 | 0.7312 | 0.5484 | 0.5484 | 0.5484 | Variable O&M, ZAR/MWh | 0.7312 | 0.7312 | 0.7312 | 0.7312 | Expense schedule, % of TPC per year | 100% | O&M cost estimates | 0 | O&M cost estimates | 0
Fuel energy content, GJ/kg | 17849.708 | 53370.0221 | 53370.0221 | 53370.0221 | 53370.0221 | 53370.0221 | 53370.0221 | 53370.0221 | Fuel energy content, GJ/kg | 1298.6681 | 1298.6681 | 1298.6681 | 1298.6681 | Fuel energy content, GJ/kg | 1298.6681 | N/A | Performance estimates |  |  | Availability estimates | 95% | 95% | 95% | 95% | 95% | Availability estimates | 92% | 92% | 92% | 92% | O&M cost estimates |  | Fixed O&M, ZAR/kW/year | 844.1 | Fixed O&M, ZAR/kW/year | 317.455
O&M cost estimates | [8 empty] | O&M cost estimates | 0 | 0 | 0 | 0 | O&M cost estimates | 0 |  | Economic life, years | 30 | 30 | Performance estimates | [5 empty] | Performance estimates |  |  |  |  | Fixed O&M, ZAR/kW/year | 665.004 | Variable O&M, ZAR/MWh | 0 | Variable O&M, ZAR/MWh | 0
Fixed O&M, ZAR/kW/year | 4998.54 | 201.85 | 423.885 | 326.63 | 500.955 | 363.33 | 3183.725 | 2321.275 | Fixed O&M, ZAR/kW/year | 2836.543 | 2626.619 | 3336.764 | 2980.407 | Fixed O&M, ZAR/kW/year | 2623.1325 | 5460.96 | Capacity factor | 49.85% | 57.26% | Economic life, years | 30 | 30 | 30 | 30 | 30 | Economic life, years | 30 | 30 | 30 | 30 | Variable O&M, ZAR/MWh | 0 | Availability estimates | 0 | Availability estimates | 0
Variable O&M, ZAR/MWh | 110.834 | 40.1865 | 80.1895 | 77.07 | 61.1055 | 57.986 | 126.0645 | 133.588 | Variable O&M, ZAR/MWh | 218.365 | 218.365 | 194.51 | 194.51 | Variable O&M, ZAR/MWh | 176.7105 | 61.1055 |  |  |  | Capacity factor (in Upington, SA) | 25.63% | 32.51% | 38.04% | 45.62% | 53.86% | Capacity factor (in Upington, SA) | 39.45% | 51% | 60.27% | 69.6% | Availability estimates | 94 | Equivalent availability | 94.1% | Equivalent availability | 90%
Availability estimates | [8 empty] | Availability estimates | 0 | 0 | 0 | 0 | Availability estimates | 0 |  |  |  |  | Water usage | [5 empty] | Water usage |  |  |  |  | Performance Estimates |  | Maintenance | 1.9% | Maintenance | 5%
Equivalent availability | 91.68% | 91.68% | 93.59% | 93.59% | 97.52% | 97.52% | 95.06% | 95.06% | Equivalent availability | 92% | 92% | 93% | 93% | Equivalent availability | 92% | 95% |  |  |  | Per unit of energy, L/MWh | 84.2424 | 80.7991 | 78.6285 | 78.1063 | 78.238 | Per unit of energy, L/MWh | 81.8912 | 87.0424 | 86.2553 | 84.5825 | Economic life, years | 30 | Unplanned outages | 4% | Unplanned outages | 5%
Maintenance | 4.8% | 4.8% | 4.5% | 4.5% | 1.5% | 1.5% | 3% | 3% | Maintenance | 6.7% | 6.7% | 5.7% | 5.7% | Maintenance | 6.7% | 4% | [14 empty] | Capacity Factor | 39% | Energy requirements, (I/O Ratio) | 1.11 | Energy requirements, (I/O Ratio) | 1.3
Unplanned outages | 3.7% | 3.7% | 2% | 2% | 1% | 1% | 2% | 2% | Unplanned outages | 1.4% | 1.4% | 1.4% | 1.4% | Unplanned outages | 1.4% | 1% | [16 empty] | Round-trip ac/ac efficiency, % | 80-90% | Round-trip ac/ac efficiency, % | 70-80%
Performance estimates | [8 empty] | Performance estimates | 0 | 0 | 0 | 0 | Performance estimates | 0 | [17 empty] | Duty cycle |  | Duty cycle
Economic life, years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Economic life, years | 30 | 30 | 30 | 30 | Economic life, years | 30 | 30 | [16 empty] | Cycles/year | 365 | Cycles/year | 365
Heat rate, kJ/kWh | 13409.7599 | 10761.5697 | 10624.4124 | 9453.3004 | 6900.0653 | 6541.3463 | 9041.8286 | 9041.8286 | Heat rate, kJ/kWh | 9999.5849 | 9999.5849 | 11249.533 | 11249.533 | Heat rate, kJ/kWh | 11500.1088 | 8510.0805 | [16 empty] | Hours/cycle | 4 | Hours/cycle | 10
Water usage | [8 empty] | Water usage, L/MWh |  |  |  |  | Water usage, L/MWh | 4.16 | Negligible | [16 empty] | Minimum load | 0 | Minimum load | 0%
Per unit of energy, L/MWh | 4469.1329 | 0 | 0 | 0 | 9.085 | 7.4951 | 0 | 0 | Cooling (once-through seawater), L/MWh | 1514 | 1514 | 1514 | 1514 | Decommissioning of existing plant* | [18 empty] | Economic life, years | 20 | Economic life, years | 60
[9 empty] | Boiler makeup, L/MWh | Negligible | Negligible | Negligible | Negligible | Total Overnight Cost, ZAR/kW | N/A | 1014.54

## Economic Parameters
https://www.resbank.co.za/content/dam/sarb/publications/statements/monetary-policy-statements/2023/march-/Statement%20of%20the%20monetary%20policy%20committee%20March%202023.pdf |  | https://data.worldbank.org/indicator/FP.CPI.TOTL.ZG?locations=GB-US | https://www.statista.com/statistics/273418/unadjusted-monthly-inflation-rate-in-the-us/ | Exchange Rate (USD or GBP) |  | https://www.resbank.co.za/en/home/what-we-do/statistics/key-statistics/selected-historical-rates
Average South Africa inflation rate for 2023 at 5.7% |  | Average US inflation rate for 2023 is 4.1%
January: 6.9% |  | January: 6.4% |  | 18.35 | ZAR/USD
February: 7.0% |  | February: 6.0% |  | 23.399 | ZAR/GBP
March: 7.1% |  | March: 5.0%
April: 6.8% |  | April: 4.9%
May: 6.3% |  | May: 4.0%
June: 5.4% |  | June: 3.0%
July: 4.7% |  | July: 3.2%
August: 4.8% |  | August: 3.7%
September: 5.0% |  | September: 3.7%
October: 5.1% |  | October: 3.2%
November: 5.5% |  | November: 3.1%
December: 5.1% |  | December: 3.4%
|  | USD | GBP
| 2016 | 1.262% | 1.008%
| 2017 | 2.13% | 2.558%
| 2018 | 2.443% | 2.293%
| 2019 | 1.812% | 1.738%
| 2020 | 1.234% | 0.9895%
| 2021 | 4.698% | 2.518%
| 2022 | 8.003% | 7.922%
| 2023 | 4.116% | 6.794%

## Learning Rates
| Fossil | [5 empty] | Nuclear | Renewables | [9 empty] | Li Ion BES | [8 empty] | REIPPPP
Base Technology | PC |  | CT | CT | CTCC | CTCC | Nuclear | Offshore Wind | Offshore Wind | Offshore Wind | Offshore Wind | Offshore Wind | Offshore Wind | Solar Thermal | Solar Thermal | Solar Thermal | Solar Thermal | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Lithium Ion | Onshore Wind | Onshore Wind | Onshore Wind | Solar PV | Solar PV | Solar PV | Solar PV | Solar PV | Solar PV
Year | Pulverized Coal (1x591 MW + 90% Carbon Capture) | Coal to Gas | Frame CT (1x297 MW, 9F.05) | Frame CT (1x540 MW, 9HA.02) | Multi-shaft CTCC (2x1 925 MW, 9F.05) | Multi-shaft CTCC (2x1 1591 MW, 9HA.02) | Small Modular Reactor (12x73 MW, SMR) | Fixed Bottom - Base Case (80x10 MW) | Fixed Bottom - Optimistic (80x10 MW) | Fixed Bottom - Conservative (80x10 MW) | Floating - Base Case (80x10 MW) | Floating - Optimistic (80x10 MW) | Floating - Conservative (80x10 MW) | Parabolic Trough (125 MW, No Storage) | Parabolic Trough w Storage (1x125 MW, 6-hr) | Parabolic Trough w Storage (1x125 MW, 12-hr) | Central Receiver w Storage (1x125 MW, 12-hr) | Lithium Ion - Base Case (100 MW/4 hr) | Lithium Ion - Optimistic (100 MW/4 hr) | Lithium Ion - Conservative (100 MW/4 hr) | Lithium Ion - Base Case (100 MW/4 hr) | Lithium Ion - Optimistic (100 MW/4 hr) | Lithium Ion - Conservative (100 MW/4 hr) | Lithium Ion - Base Case (100 MW/4 hr) | Lithium Ion - Optimistic (100 MW/4 hr) | Lithium Ion - Conservative (100 MW/4 hr) | Onshore Wind (BW6) Conservative | Onshore Wind (BW6) Base Case | Onshore Wind (BW6) Optimistic | Solar PV (BW6 Preferred) Conservative | Solar PV (BW6 Preferred) Base Case | Solar PV (BW6 Preferred) Optimistic | Solar PV (BW6 Compliant) Conservative | Solar PV (BW6 Compliant) Base Case | Solar PV (BW6 Compliant) Optimistic
| 161310.591 |  | 13987.9203 | 12024.3912 | 20497.5549 | 15754.7857 | 161529.2405 | 84996.9582 | 89241.0674 | 79917.5708 | 125891.5322 | 132177.609 | 118368.2999 | 90847.3561 | 147104.5231 | 212977.2529 | 173602.4607 | 37826.9794 | 33389.6241 | 29496.9523 | 37305.6489 | 48439.3181 | 32298.7301 | 37387.5671 | 45841.2138 | 30374.8957
2023 | 149567.18 |  | 12980.79 | 11158.635 | 18652.775 | 14336.855 | 153378.475 | 72427.2894 | 72427.2894 | 72427.2894 | 107274.2205 | 107274.2205 | 107274.2205 | 83198.0087 | 134718.3223 | 195044.5682 | 158985.1336 | 25910.2 | 25910.2 | 25910.2 | 25910.2 | 25910.2 | 25910.2 | 25910.2 | 25910.2 | 25910.2
2024 | 148341.2195 |  | 12645.0799 | 10870.0496 | 18037.8484 | 13864.2114 | 151469.1994 | 69728.8076 | 68354.3309 | 70967.7215 | 103277.4185 | 101241.64 | 105112.4109 | 82162.3488 | 133041.3307 | 192616.6275 | 157006.0655 | 24631.1423 | 24474.2516 | 25184.8745 | 24041.8795 | 23637.8427 | 25910.2 | 24134.4721 | 23782.2362 | 24717.5714 | 26647.47 | 26647.47 | 26647.47 | 15715.17 | 15715.17 | 15715.17 | 19756.22 | 19756.22 | 19756.22
2025 | 147115.259 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 149559.9238 | 67100.6689 | 64596.1729 | 69602.7923 | 99384.8038 | 95675.3201 | 103090.7735 | 81126.689 | 131364.3391 | 190188.6868 | 155026.9974 | 23425.7102 | 23133.6955 | 24665.8735 | 22441.7709 | 21694.7387 | 24648.6049 | 22596.3801 | 21943.1531 | 23676.9796 | 25470.4163 | 26200.1041 | 26297.6223 | 14921.5292 | 15192.6886 | 15518.6922 | 18758.4998 | 19099.3861 | 19509.2192
2026 | 145938.3369 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 146867.8451 | 64688.4579 | 61116.5216 | 68541.1622 | 95812.0061 | 90521.5046 | 101518.3614 | 80153.1687 | 129787.9671 | 187906.4226 | 153166.6735 | 22808.4746 | 22525.3339 | 24443.0986 | 21034.3257 | 19988.4181 | 23553.5451 | 21313.1028 | 20426.3786 | 22826.2079 | 24245.9098 | 25695.3137 | 26093.2164 | 14062.0001 | 14730.6427 | 15322.2144 | 17677.9486 | 18518.5281 | 19262.2185
2027 | 144761.4149 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 144175.7665 | 62475.6099 | 57890.2586 | 67561.6892 | 92534.4909 | 85742.9903 | 100067.6347 | 79179.6484 | 128211.595 | 185624.1584 | 151306.3495 | 22216.4934 | 21943.1162 | 24237.433 | 19718.2033 | 18418.331 | 22509.1173 | 20110.7668 | 19026.8324 | 22016.3416 | 22973.7498 | 25169.9424 | 25894.2365 | 13213.2627 | 14244.5514 | 15125.7365 | 16610.9641 | 17907.4417 | 19015.2177
2028 | 143584.4928 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 141483.6879 | 60443.8271 | 54902.4526 | 66658.7168 | 89525.1567 | 81317.6615 | 98730.2154 | 78206.1282 | 126635.2229 | 183341.8941 | 149446.0255 | 21679.0934 | 21385.8024 | 24048.5337 | 19055.533 | 16973.4828 | 21833.8437 | 19467.7806 | 17735.2037 | 21479.84 | 21657.6953 | 24622.6461 | 25681.6955 | 12376.906 | 13761.2698 | 14929.2587 | 15559.5439 | 17299.8875 | 18768.2169
2029 | 142407.5707 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 138791.6092 | 58584.0981 | 50428.7626 | 65826.7987 | 86770.6566 | 74691.5458 | 97498.0366 | 77232.6079 | 125058.8509 | 181059.6299 | 147585.7016 | 21162.022 | 20852.2148 | 23876.0737 | 18415.816 | 15643.7728 | 21178.8284 | 18847.3353 | 16542.9323 | 20961.915 | 20299.7637 | 24055.7868 | 25430.052 | 11549.6287 | 13285.6977 | 14732.7809 | 14519.5378 | 16702.0253 | 18521.2162
2030 | 141230.6487 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 136099.5306 | 55039.2103 | 47930.4005 | 65060.6308 | 81520.2175 | 70991.1471 | 96363.2425 | 76259.0876 | 123482.4788 | 178777.3656 | 145725.3776 | 20664.4475 | 20341.2344 | 23815.616 | 17798.2293 | 15016.4668 | 20537.9542 | 18248.6064 | 15935.7082 | 20480.1154 | 18904.4079 | 23472.7097 | 25188.6757 | 10729.0348 | 12818.1451 | 14536.3031 | 13487.9337 | 16114.2447 | 18274.2154
2031 | 140806.9567 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 133105.3409 | 53548.402 | 44208.4551 | 64484.1073 | 79312.1368 | 65478.4626 | 95509.3364 | 75343.9786 | 122000.689 | 176632.0372 | 143976.6731 | 20337.9115 | 20293.9314 | 23815.616 | 17452.0457 | 14880.6561 | 20537.9542 | 17905.5101 | 15815.177 | 20480.1154 | 18585.3733 | 23232.2139 | 25072.8594 | 10453.7018 | 12582.6206 | 14306.392 | 13141.8008 | 15818.1567 | 17985.1843
2032 | 140383.2648 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 130111.1513 | 50620.9647 | 42121.1189 | 63962.9995 | 74976.222 | 62386.8467 | 94737.508 | 74428.8695 | 120518.8993 | 174486.7089 | 142227.9685 | 20017.0387 | 19973.6359 | 23815.616 | 17112.6879 | 14591.5151 | 20537.9542 | 17569.057 | 15520.6576 | 20480.1154 | 18274.6039 | 22986.0169 | 24982.7422 | 10187.4946 | 12357.5724 | 14076.4809 | 12807.1401 | 15535.2388 | 17696.1531
2033 | 139959.5728 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 127116.9616 | 49442.9827 | 40879.5848 | 63492.2301 | 73231.4777 | 60547.9734 | 94040.2374 | 73513.7605 | 119037.1096 | 172341.3805 | 140479.264 | 19701.7245 | 19658.8904 | 23815.616 | 16780.0205 | 14308.0722 | 20537.9542 | 17239.1163 | 15231.8108 | 20480.1154 | 17972.9413 | 22745.9114 | 24899.0158 | 9932.1808 | 12138.1554 | 13846.5699 | 12486.1741 | 15259.4002 | 17407.122
2034 | 139535.8809 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 124122.7719 | 48403.614 | 39768.4573 | 63066.7625 | 71692.0377 | 58902.2494 | 93410.0647 | 72598.6514 | 117555.3198 | 170196.0521 | 138730.5595 | 19391.8663 | 19349.5926 | 23815.616 | 16453.9105 | 14030.2143 | 20537.9542 | 16915.56 | 14948.5253 | 20480.1154 | 17674.5123 | 22515.0354 | 24813.6789 | 9683.6783 | 11925.6708 | 13616.6588 | 12173.7709 | 14992.2766 | 17118.0908
2035 | 139112.1889 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 121128.5822 | 47475.6243 | 38721.114 | 62681.5916 | 70317.5645 | 57350.9978 | 92839.5766 | 71683.5424 | 116073.5301 | 168050.7237 | 136981.8549 | 19087.3635 | 19045.6419 | 23815.616 | 16134.2279 | 13757.8305 | 20537.9542 | 16598.2626 | 14670.692 | 20480.1154 | 17378.5357 | 22284.645 | 24735.5363 | 9443.9324 | 11714.3928 | 13386.7477 | 11872.3759 | 14726.67 | 16829.0597
2036 | 138694.8524 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 117979.2391 | 46586.1274 | 37568.9058 | 62331.7368 | 69000.104 | 55644.428 | 92321.3962 | 71248.1189 | 115368.471 | 167029.9424 | 136149.7936 | 18788.1174 | 18746.9398 | 23815.616 | 15820.8449 | 13490.8122 | 20537.9542 | 16287.1011 | 14398.2039 | 20480.1154 | 17085.3396 | 22055.2906 | 24674.4279 | 9209.5912 | 11521.5993 | 13156.8367 | 11577.7754 | 14484.3009 | 16540.0285
2037 | 138277.5158 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 114829.896 | 45536.4873 | 36772.7393 | 62012.2371 | 67445.4507 | 54465.202 | 91848.1755 | 70812.6955 | 114663.4119 | 166009.1611 | 135317.7322 | 18494.0312 | 18453.3897 | 23815.616 | 15513.6366 | 13229.0528 | 20537.9542 | 15981.9547 | 14130.9564 | 20480.1154 | 16794.9015 | 21830.5997 | 24638.3745 | 8984.674 | 11332.6495 | 12926.9256 | 11295.0223 | 14246.7639 | 16250.9974
2038 | 137860.1792 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 111680.5528 | 44880.4758 | 36049.7214 | 61718.147 | 66473.8125 | 53394.3185 | 91412.59 | 70377.2721 | 113958.3528 | 164988.3798 | 134485.6708 | 18205.01 | 18164.8967 | 23815.616 | 15212.4804 | 12972.4481 | 20537.9542 | 15682.7053 | 13868.8466 | 20480.1154 | 16504.7316 | 21607.3698 | 24610.8484 | 8763.0458 | 11145.463 | 12697.0145 | 11016.404 | 14011.4437 | 15961.9662
2039 | 137442.8427 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 108531.2097 | 44284.237 | 35389.6326 | 61444.5343 | 65590.7054 | 52416.6414 | 91007.334 | 69941.8487 | 113253.2937 | 163967.5984 | 133653.6094 | 17920.9606 | 17881.3678 | 23815.616 | 14917.2561 | 12720.8957 | 20537.9542 | 15389.2369 | 13611.774 | 20480.1154 | 16216.037 | 21383.3862 | 24570.3888 | 8548.7854 | 10958.6292 | 12467.1035 | 10747.0479 | 13776.5669 | 15672.9351
2040 | 137025.5061 |  | 12309.3698 | 10581.4642 | 17422.9217 | 13391.5679 | 105381.8666 | 43732.4673 | 34789.0522 | 61186.4768 | 64773.4628 | 51527.1038 | 90625.1173 | 69506.4253 | 112548.2346 | 162946.8171 | 132821.548 | 17641.7917 | 17602.7118 | 23815.616 | 14627.8461 | 12474.2954 | 20537.9542 | 15101.4361 | 13359.6397 | 20480.1154 | 15934.4774 | 21156.6188 | 24521.6786 | 8341.357 | 10770.8841 | 12237.1924 | 10486.2807 | 13540.5443 | 15383.9039